Digital Twin for Campus Energy and Space

Functional Requirements

Deliverable #1

1. Definition

Functional requirements are the activities the system must perform: the business uses and functions that users carry out. Use cases define them, because each use case is an activity the system performs, usually in response to a request by a user.

2. Functional requirements

| ID | Activity (use case) | The system shall… |
| --- | --- | --- |
| FR-1 | Register Campus Structure | Let facilities staff register and update buildings, floors, rooms (with type, capacity, area and a critical-room flag), equipment, and sensors. |
| FR-2 | Collect sensor data | Accept data from all sensors about temperature, humidity, CO2, occupancy, and energy once in 5 minutes and keep them for 3 years. |
| FR-3 | Detect faults | Detect any sensor or equipment that stopped sending data, broke down, or started sending unrealistic values; create a ticket for maintenance; notify the responsible staff about the fault and about whom to contact |
| FR-4 | Import timetable | Let the registrar import the semester timetable as bookings. |
| FR-5 | Book a room | Let students and staff book a free room for up to 2 hours for study or meetings, in Arabic or English, rejecting double bookings and groups that don’t fit the room. |
| FR-6 | Cancel a booking | Let users cancel or release a booking. |
| FR-7 | Detect no-shows | Compare bookings with real occupancy, mark a room still empty 20 minutes after the start as a “no show”, and remind instructors with repeated “no shows”. |
| FR-8 | Control air conditioning | Switch the air conditioner on 15 minutes before a booking and off after 15 empty minutes, keep temperature within the policy range, and reduce corridor cooling in peak hours. |
| FR-9 | Respond to poor environment conditions | Increase ventilation when a room is too hot or CO2 rises above 1,000 ppm and alert Facilities if the problem continues. |
| FR-10 | Override settings | Let authorized staff override a room’s settings, log each override, end it after 2 hours, and report repeated overrides. |
| FR-11 | Protect critical rooms | Exclude critical rooms from all energy saving rules and raise a temperature alarm for them. |
| FR-12 | Run a what-if scenario | Let managers create a scenario (for example, moving lectures into one building) and see its estimated energy cost, room use, and comfort. |
| FR-13 | Analyze energy and room usage | Show energy usage over time, the energy wasted cooling empty rooms each month, rooms booked but rarely used, and rooms with poor air quality most often. |
| FR-14 | Generate reports | Produce the monthly energy report for each building for the President’s office; the yearly carbon report for the sustainability office, a report of savings against the 20% target during the pilot, and consumption data for the electricity utility’s billing. |
| FR-15 | View the live campus | Show a 3D campus map with live energy and occupancy colors and dashboards of energy use, occupancy, and alerts in the office and on phones. |
| FR-16 | Find a free room | Show free rooms on a map in real time, in Arabic or English, including which buildings have accessible entrances. |
| FR-17 | Control building equipment | Read from and send commands to the building management system through the BACnet gateway. |